## Table B2.1
Table B2.1: Regulations for water reuse in toilet flushing.
FROM WASTEWATER TO TOILET FLUSHING
PARAMETER | Odour | pH | Color | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TDS | TOC | NH4-N | T.N | Detergents | Fe | Mn | T. Coliform (max single sample) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo tolerant coliforms | Intestinal Nematodes | Coliphages | Clostridia
COUNTRY |  |  |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10 L | pfu/100mL | cfu/100mL
EPA |  | 6 - 9 |  | 2 | 1 |  | 10 | [15 empty] | 0
Texas, USA |  |  |  | 3 |  |  | 5 | [12 empty] | 75 | 20 | 75 | 20 |  | 4
Florida, USA |  |  |  | 5 | 1 |  | 20 | 10 | 5 |  | 5 |  | 12 | [8 empty] | 25
Spain |  |  |  | 2 |  |  |  | 10 | [11 empty] | 0 | [7 empty] | 1
China |  |  | 30 | 5 | 0.2 - 1 |  | 10 |  |  | 1500 |  | 10 | 10 | 1 | 0.3 | 0.1 | [5 empty] | 3
Japan |  | 5.8 - 8.6 |  | 2 | 0.1 - 0.4 | [14 empty] | 0
|  | 6 - 9 |  | 5 |  |  | 10 | [9 empty] | 10 |  |  |  |  | 10
Korea | Non offensive | 5.8 - 8.5 |  | 5 |  |  | 10 | [9 empty] | 10
Saudi Arabia | [5 empty] | 15 | 10 (30d) | 15 (7d) | 10 | [12 empty] | 23 |  | 2.2 |  |  |  | 1
Brazil |  |  |  | 10 | [17 empty] | 500
Western Australia, Australia |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 |  | 10 | 10 | [11 empty] | 1 | [8 empty] | 1 | 1
Tasmania, Australia |  | 5.5 - 8.0 |  |  |  |  | 10 | [19 empty] | 10
FROM GREY WATER TO TOILET FLUSHING
PARAMETER | Odour | pH | Color | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TDS | TOC | NH4-N | T.N | Detergents | Fe | Mn | T. Coliform (max single sample) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo tolerant coliformsc | Intestinal Nematodes | Coliphages | Clostridia
COUNTRY |  |  |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10 L | pfu/100mL | cfu/100mL
California, USA |  |  |  | 2 | [12 empty] | 23 | 2.2
Texas, USA | [7 empty] | 30 | 10 | [10 empty] | 200 | 2.2
New Mexico, USA | [6 empty] | 30 | 30 | [11 empty] | 126
Georgia, USA |  |  |  | 10 | [12 empty] | 500 |  |  |  |  | 100
Colorado, USA |  |  |  |  | 0.2 - 4
Hawaii, USA | [21 empty] | 200 | 23 | 2.2
Nevada, USA | [6 empty] | 30 | [14 empty] | 23
Arizona, USA |  |  |  | 2 - 5 | [17 empty] | 23
Massachusetts, USA |  | 6.5 - 8.5 |  | 2 |  |  | 10 | 5 |  |  |  |  | 10 | [8 empty] | 14 |  | 0
Oregon, USA | [6 empty] | 10 | 10 | [8 empty] | 2.2
Wisconsin, USA |  | 6 - 9 |  |  | 0.1 - 4 |  |  | 5
Washington, USA |  |  |  | 2 - 5 |  |  | 5 | 5 |  |  | 1 |  | 10 |  |  |  | 23 |  | 2.2
Montana, USA | No quality criteria.
South Dakota, USA | No quality criteria.
Singapore | Non | 6 - 9 | 15 HU | 2 | 0.5 - 2 |  | 5 | [9 empty] | 10 |  |  | 0
Germany | [6 empty] | 5 | [9 empty] | 100 |  |  |  |  | 10
Canada |  |  |  | 5 | 0.5 |  | 20 | 20 | [11 empty] | 200 | 0 | [5 empty] | 200
United Kingdom |  | 5 - 9.5 |  | 10 | 2 | [11 empty] | 1000
Israel |  |  |  | 10 - 20 | 0.4 - 0.6 | [16 empty] | 400 | 100 (1 y)
Jordon | [6 empty] | 10 | 10 | [13 empty] | 10
Victoria, Australia | [6 empty] | 10 | 10 | [11 empty] | 10
New South Wales, Australia | [6 empty] | 20 | 30 | [11 empty] | 10
Northern Territory, Australia |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 |  | 10 | 10 | [12 empty] | 1(1y) | [7 empty] | 1 | 1
Queensland, Australia |  | 6.5 - 8.5 |  | 1 - 5 | 0.2 - 1 |  | 10 | 10 | [11 empty] | 10 | 1(1y) | [5 empty] | 10