## Table B2.2
Table B2.2: Regulations for water reuse in cooling.
FROM WASTEWATER TO COOLING
PARAMETER | Notes | Odour | pH | Color | Turbidity | Residual Cl | BOD | TSS | TOC | T.N | T. Coliform (max single) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo. coliforms | Intestinal Nematodes | T.Legionella
COUNTRY |  |  |  | HU | NTU | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10 L | cfu/L
WHO
EPA | Once-through cooling |  | 6 - 9 |  |  | 1 | 30 | 30 | [7 empty] | 200
| Recirculating cool. towers |  | 6 - 9 |  |  | 1 | 30 | 30 | [7 empty] | 200
Spain |  |  |  |  | 1 |  |  | 5 |  |  |  |  | 0 | [7 empty] | 1
Texas, USA | Cooling tower make up | [5 empty] | 20 | [5 empty] | 800 | 200 | 800 | 200 |  | 89 | 35
New Jersey, USA | Non-contact cooling water | Permit levels must be met
Georgia, USA | Industrial reuse |  | 6 - 9 |  | 3 |  | 5 | 5 | [6 empty] | 100 | 23 | 46
Western Australia, Australia |  |  | 6.5 - 8.5 |  | 5 | 0.2 - 2 | 20 | 30 |  |  |  |  | 10
Tasmania, Australia | Ind.(open system) |  | 5.5 - 8.0 |  |  |  | 50 | [12 empty] | 1000
| Ind.(closed system) |  | 5.5 - 8.0 |  |  |  | 80 | [12 empty] | 10000
FROM GREY WATER TO COOLING
PARAMETER | Notes | Odour | pH | Color | Turbidity | Residual Cl | BOD | TSS | TOC | T.N | T. Coliform (max single) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo. coliforms | Intestinal Nematodes | T.Legionella
COUNTRY |  |  |  | HU | NTU | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10 L | cfu/L
California, USA | Cooling |  |  |  | 2
Oregon, USA | Industrial cooling | [5 empty] | 10 | 10 |  |  | 23 | 2.2
Hawaii, USA | Cooling sys. with tower |  |  |  | 5 - 10 | [9 empty] | 200 | 23 | 2.2
Massachusetts, USA | Cooling towers |  | 6.5 - 8.5 |  | 2 |  | 10 | 5 |  | 10 |  |  |  |  | 14 |  | 0
Washington, USA | Cooling (aerosol created) |  |  |  | 2 - 5 |  | 5 | 5 | 1 | 10 | 23 | 2.2
| Cooling (No aerosol) |  |  |  | 2 - 5 |  | 5 | 5 | 1 | 10 | 240 | 23
Wisconsin, USA |  |  | 6 - 9 |  |  | 1 - 10 | 50 | 30
Singapore | Cooling towers | Non | 6 - 9 | 15 | 2 | 0.5 - 2 | 5 |  |  |  | 10 |  | 0 | [8 empty] | 1000
Victoria, Australia |  | Prohibited.
Northern Territory, Australia |  |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 | 20 | 30 | [5 empty] | 10(1y)