## Table B2.3
Table B2.3: Regulations for water reuse in landscape irrigation.
FROM WASTEWATER TO LANDSCAPE IRRIGATION
PARAMETER |  | Odour | pH | Color | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TDS | TOC | NH4-N | T.N | Detergents | T. Coliform (max single) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo. coliforms | Intestinal Nematodes | Coliphages | Clostridia
COUNTRY |  |  |  |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10L | pfu/100mL | cfu/100mL
EPA | Landscape |  | 6 - 9 |  | 2 | 1 |  | 10 | [13 empty] | 0
New Jersey, USA | Public access systems |  |  |  | 2 | 1 |  |  | 5 |  |  |  |  | 10 | [6 empty] | 14 |  | 2.2
Texas, USA | Residential irrigation |  |  |  | 3 |  |  | 5 | [10 empty] | 75 | 20 | 75 | 20 |  | 9 | 4
Georgia, USA | Drip irrigation | [6 empty] | 25 | 25
| Residential areas |  | 6 - 9 |  | 3 |  |  | 5 | 5 | [11 empty] | 100 | 23 | 46
China | Irrigation of green |  |  | 30 | 20 | 0.2 - 1 |  | 20 |  |  | 1000 |  | 20 |  | 1 | [5 empty] | 3
Japan | Landscape use | Non offensive | 5.8 - 8.6 | 40 | 2 | [13 empty] | 1000
Korea | Sprinklers | Non offensive | 5.8 - 8.5 |  | 5 | 0.2 |  | 10 | [7 empty] | 0
| Gardening | Non offensive | 5.8 - 8.5 |  | 10 |  |  | 10 | [7 empty] | 0
Greece | Unrestricted irrigation |  | 6.5 - 8.5 |  | 2 |  |  | 10 - 25 | 35 |  | 2000 |  |  | 30 |  |  | 2 |  |  |  | 200
Italy | Irrigation of green areas |  | 6 - 9.5 |  |  |  |  | 20 | 10 |  |  |  |  | 15 | [5 empty] | 10
France | Irrigation of green areas | [7 empty] | 15 | [9 empty] | 250
Portugal | Irrigation |  | 6.5 - 8.4 | [5 empty] | 60 |  | 640 | [10 empty] | 100 |  |  |  |  | 1
Brazil | Irrigation of green areas |  |  |  | 5 | 0.5 | [14 empty] | 500
Spain | Private gardens |  |  |  | 2 |  |  |  | 10 | [9 empty] | 0 | [7 empty] | 1
| Urban Areas |  |  |  | 10 |  |  |  | 20 | [9 empty] | 200 | [7 empty] | 1
Saudi Arabia | Unrestricted access area | [5 empty] | 15 | 10 (30d) | 15 (7d) | 10 | [10 empty] | 23 |  | 2.2 |  |  |  | 1
Cyprus | Irrigation |  |  |  | 20 | [16 empty] | 50
Turkey* |  |  | 6 - 9 |  | 2 - 5 | 1 |  | 20 | 30 |  | 500 | [9 empty] | 0
Western Australia, Australia | External surface |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 |  | 10 | 10 | [9 empty] | 1 | [8 empty] | 1 | 1
| Urban/restricted access |  | 6.5 - 8.5 |  | 5 | 0.2 - 2 |  | 20 | 30 | [9 empty] | 10
| Communal sub-surface |  | 6.5 - 8.5 |  |  | 0.2 - 2 |  | 20 | 30 | [9 empty] | 1000
Tasmania, Australia | Non-potable municipal/uncontrolled access, garden watering |  | 5.5 - 8.0 |  |  |  |  | 10 | [17 empty] | 10
FROM GREY WATER TO LANDSCAPE IRRIGATION
PARAMETER |  | Odour | pH | Color | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TDS | TOC | NH4-N | T.N | Detergents | T. Coliform (max single) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Thermo. coliforms | Intestinal Nematodes | Coliphages | Clostridia
COUNTRY |  |  |  |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL | egg/10L | pfu/100mL | cfu/100mL
California, USA | Irrigation |  |  |  | 2 | [10 empty] | 23 | 2.2
Hawaii, USA | Spray, Drip, Subsurface |  |  |  | 5 - 10 | [15 empty] | 200 | 23 | 2.2
| Subsurface |  |  |  | 5 - 10 | [15 empty] | 200 |  | 23
Texas, USA | Public access | [17 empty] | 75 | 20
New Mexico, USA | Subsurface irigation | [6 empty] | 30 | 30
Oregon, USA | Type 1: Subsurface | No quality criteria.
| Type 2: Surface drip | [6 empty] | 10 | 10
| Type 3: Sprinkler | [6 empty] | 10 | 10 | [6 empty] | 23 |  | 2.2
Nevada, USA | Garden irrigation | [6 empty] | 30 | [12 empty] | 23
Arizona, USA | Residential/open access landscape irrigation |  |  |  | 2 - 5 | [15 empty] | 23
Massachusetts, USA | Landscape around residential areas |  | 6.5 - 8.5 |  | 2 |  |  | 10 | 5 |  |  |  |  | 10 | [6 empty] | 14 |  | 0
Washington, USA | Open access areas |  |  |  | 2 - 5 |  |  | 5 | 5 |  |  | 1 |  | 10 |  | 23 |  | 2.2
Colorado, USA |  | No quality criteria.
South Dakota, USA |  | No quality criteria.
Montana, USA |  | No quality criteria.
Utah, USA |  | No quality criteria.
Singapore | Excluding sprinklers | Non | 6 - 9 | 15 HU | 2 | 0.5 - 2 |  | 5 | [7 empty] | 10 |  |  | 0
Germany | Garden | [6 empty] | 5 | [7 empty] | 100 |  |  |  |  | 10
United Kingdom | Garden |  | 5 - 9.5 |  | 10 | 2 | [10 empty] | 1000
| Spray |  | 5 - 9.5 |  | 10 | 0.5 | [10 empty] | 10
Israel | Green grass, lawn |  |  |  | 5 - 10 | 0.6 - 1 | [14 empty] | 40 | 10 (1 y)
Jordon | Spor field, public parks, public lawns and ornamental use | [6 empty] | 10 | 10 | [11 empty] | 10
Victoria, Australia | Garden | [6 empty] | 20 | 30 | [9 empty] | 10
[8 empty] | 10 | 10 | [9 empty] | 10
New South Wales, Australia | Surface | [6 empty] | 20 | 30 | [9 empty] | 30
Northern Territory, Australia | External surface |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 |  | 10 | 10 | [10 empty] | 1 (1y) | [7 empty] | 1 | 1
| Urban/unrestricted access |  | 6.5 - 8.5 |  | 2 - 5 | 0.2 - 2 |  | 20 | 30 | [10 empty] | 10 (1y)
Queensland, Australia | Lawn and garden via spray |  | 6.5 - 8.5 |  | 5 | 0.2 - 1 |  | 10 | 10 | [9 empty] | 100 | 10 (1y) | [5 empty] | 30
| Lawn and garden via drip or subsurface | [6 empty] | 20 | 30 | [9 empty] | 1000 | 100(1y)
| Lawn and garden via sub-surface (bucketing) | [6 empty] | 240 | 180