## Table B2.6
Table B2.6: Regulations for water reuse in fire protection.
FROM WASTEWATER TO FIRE PROTECTION
PARAMETER | pH | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TOC | T.N | T. Coliform (max single) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Intestinal Nematodes | Thermo. coliforms
COUNTRY |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | egg/10L | cfu/100 mL
WHO
EPA | 6 - 9 | 2 | 1 |  | 10 | [9 empty] | 0
Spain |  | 10 |  |  |  | 20 | [6 empty] | 200 | [6 empty] | 1
Saudi Arabia |  |  |  | 15 | 10 (30d) | 15 (7d) | 10 | [7 empty] | 23 |  | 2.2 |  |  | 1
Texas, USA |  | 3 |  |  | 5 | [7 empty] | 75 | 20 | 75 | 20 |  | 9 | 4
Florida, USA |  | 5 | 1 |  | 20 | 5 | [8 empty] | 25
New Jersey, USA | [5 empty] | 5 | [9 empty] | 200 | 400
Georgia, USA | 6 - 9 | 3 |  |  | 5 | 5 | [8 empty] | 100 | 23 | 46
Tasmania, Australia | 5.5 - 8.0 |  |  |  | 10 | [15 empty] | 10
Western Australia, Australia | 6.5 - 8.5 | 5 | 0.2 - 2 |  | 20 | 30 | [6 empty] | 10
FROM GREY WATER TO FIRE PROTECTION
PARAMETER | pH | Turbidity | Residual Cl | BOD (7d mean) | BOD (max single) | TSS (max single) | TSS (30d mean) | TOC | T.N | T. Coliform (max single) | T. Coliform (30d mean) | T. Coliform (7d mean) | E.Coli (max single) | E.Coli (30d mean) | Faecal Coli. (max single) | Faecal Coli. (30d mean) | Faecal Coli. (7d mean) | Enterococci (max single) | Enterococci (30d mean) | Intestinal Nematodes | Thermo. coliforms
COUNTRY |  | NTU | mg/L | mg/L |  | mg/L |  | mg/L | mg/L | cfu/100 mL |  |  | cfu/100 mL |  | cfu/100 mL |  |  | cfu/100 mL |  | egg/10L | cfu/100 mL
Washington, USA |  | 2 - 5 |  |  | 5 | 5 |  | 1 | 10 | 23 |  | 2.2
Arizona, USA |  | 2 - 5 | [12 empty] | 23
Hawaii, USA |  | 5 - 10 | [12 empty] | 200 | 23 | 2.2 |  |  |  |  | R1
|  | 5 - 10 | [12 empty] | 200 |  | 23 |  |  |  |  | R2
Massachusetts, USA | 6.5 - 8.5 | 2 |  |  | 10 | 5 |  |  | 10 | [5 empty] | 14 |  | 0
New Mexico, USA |  |  |  |  | 30 | 30 | [7 empty] | 126
Northern Territory, Australia | 6.5 - 8.5 | 2 - 5 | 0.2 - 2 |  | 20 | 30 | [7 empty] | 10(1y)